## MAGNATRON A.C. SAVER DATA
MAGNATRON A.C. SAVER DATA
Date | Mode | Capacity (TR) | Room Temperature set point(* C) | Avg. Ambient temperature (*C) | Per day Consumption (KWH) | Avg. on/off cycle per hour | Max. on/off cycle per hour
25/10/2014 | Bypass | 1.5 | 26 | 28.6 | 10.2 | 5 | 12
29/10/2014 | Bypass |  |  | 28.8 | 11.3 | 7 | 12
2014-02-11 | Bypass |  |  | 28.9 | 11 | 7 | 12
26/10/2014 | Saver | 1.5 | 26 | 28.9 | 7.5 | 6 | 10
28/10/2014 | Saver |  |  | 28.5 | 8.1 | 4 | 8
2014-01-11 | Saver |  |  | 28.6 | 7.7 | 3 | 5
TOTAL BY PASS MODE 32.5 KWH
TOTAL SAVINGS MODE 23.3 KWH
| Bypass | Saver |  |  | SAVINGS 9.2 KWH=28.3%
25/10/2014 | 10.2 |  |  |  | R.O.I =88 DAYS PRE-DEPRECIATION & 58 DAYS
29/10/2014 | 11.3 |  |  |  | POST -DEPRECIATION.
2014-02-11 | 11 |  |  |  | TEMPERATURE IS SAME WITH &WITHOUT
26/10/2014 |  | 7.5 |  |  | AC SAVER-THUS, SAVINGS ARE NOT AT THE COST
28/10/2014 |  | 8.1 |  |  | TEMPERATURE
2014-01-11 |  | 7.7 |  |  | BOTH MAXIMUM & AVERAGE CYCLES PER
HAVE REDUCED SUBSTANTIALLY ,THUS INCREASING
THE LIFE OF COMPRESSOR, REDUCING RUN-TIME
& MAINTENANCE COST.

## ON OFF Details
AC Mode : Bypass | [11 empty] | AC Mode : Saver
Hourly compressor On/Off (26/10/14) |  |  |  | Hourly compressor On/Off (28/10/14) |  |  |  | Hourly compressor On/Off (1/11/14) |  |  |  | Hourly compressor On/Off (25/10/14) |  |  |  | Hourly compressor On/Off (29/10/14) |  |  |  | Hourly compressor On/Off (2/11/14)
Time Slot |  |  | Hourly ON/OFF | Time Slot |  |  | Hourly ON/OFF | Time Slot |  |  | Hourly ON/OFF | Time Slot |  |  | Hourly ON/OFF | Time Slot |  |  | Hourly ON/OFF | Time Slot |  |  | Hourly ON/OFF
12:00 | to | 13:00 | 4 | 12:00 | to | 13:00 | 4 | 12:00 | to | 13:00 | 3 | 12:00 | to | 13:00 | 4 | 12:00 | to | 13:00 | 12 | 12:00 | to | 13:00 | 3
13:00 | to | 14:00 | 3 | 13:00 | to | 14:00 | 4 | 13:00 | to | 14:00 | 4 | 13:00 | to | 14:00 | 12 | 13:00 | to | 14:00 | 12 | 13:00 | to | 14:00 | 11
14:00 | to | 15:00 | 4 | 14:00 | to | 15:00 | 3 | 14:00 | to | 15:00 | 4 | 14:00 | to | 15:00 | 11 | 14:00 | to | 15:00 | 11 | 14:00 | to | 15:00 | 12
15:00 | to | 16:00 | 4 | 15:00 | to | 16:00 | 3 | 15:00 | to | 16:00 | 3 | 15:00 | to | 16:00 | 8 | 15:00 | to | 16:00 | 10 | 15:00 | to | 16:00 | 10
16:00 | to | 17:00 | 4 | 16:00 | to | 17:00 | 3 | 16:00 | to | 17:00 | 3 | 16:00 | to | 17:00 | 0 | 16:00 | to | 17:00 | 10 | 16:00 | to | 17:00 | 6
17:00 | to | 18:00 | 4 | 17:00 | to | 18:00 | 3 | 17:00 | to | 18:00 | 4 | 17:00 | to | 18:00 | 0 | 17:00 | to | 18:00 | 10 | 17:00 | to | 18:00 | 0
18:00 | to | 19:00 | 2 | 18:00 | to | 19:00 | 3 | 18:00 | to | 19:00 | 4 | 18:00 | to | 19:00 | 0 | 18:00 | to | 19:00 | 10 | 18:00 | to | 19:00 | 0
19:00 | to | 20:00 | 0 | 19:00 | to | 20:00 | 4 | 19:00 | to | 20:00 | 5 | 19:00 | to | 20:00 | 3 | 19:00 | to | 20:00 | 11 | 19:00 | to | 20:00 | 0
20:00 | to | 22:00 | 2 | 20:00 | to | 21:00 | 2 | 20:00 | to | 21:00 | 6 | 20:00 | to | 21:00 | 4 | 20:00 | to | 22:00 | 22 | 20:00 | to | 22:00 | 12
22:00 | to | 0:00 | 18 | 21:00 | to | 22:00 | 0 | 21:00 | to | 22:00 | 6 | 21:00 | to | 22:00 | 4 | 22:00 | to | 0:00 | 20 | 22:00 | to | 0:00 | 19
0:00 | to | 2:00 | 20 | 22:00 | to | 0:00 | 8 | 22:00 | to | 0:00 | 10 | 22:00 | to | 0:00 | 17 | 0:00 | to | 2:00 | 15 | 0:00 | to | 2:00 | 19
2:00 | to | 4:00 | 20 | 0:00 | to | 2:00 | 10 | 0:00 | to | 2:00 | 4 | 0:00 | to | 2:00 | 16 | 2:00 | to | 4:00 | 12 | 2:00 | to | 4:00 | 18
4:00 | to | 6:00 | 18 | 2:00 | to | 4:00 | 8 | 2:00 | to | 4:00 | 0 | 2:00 | to | 4:00 | 16 | 4:00 | to | 6:00 | 11 | 4:00 | to | 6:00 | 18
6:00 | to | 8:00 | 14 | 4:00 | to | 6:00 | 12 | 4:00 | to | 6:00 | 0 | 4:00 | to | 6:00 | 13 | 6:00 | to | 8:00 | 4 | 6:00 | to | 8:00 | 17
8:00 | to | 10:00 | 14 | 6:00 | to | 8:00 | 16 | 6:00 | to | 8:00 | 0 | 6:00 | to | 8:00 | 6 | 8:00 | to | 10:00 | 3 | 8:00 | to | 10:00 | 17
10:00 | to | 12:00 | 14 | 8:00 | to | 10:00 | 11 | 8:00 | to | 10:00 | 7 | 8:00 | to | 10:00 | 1 | 10:00 | to | 11:00 | 4 | 10:00 | to | 0:00 | 15
|  |  |  | 10:00 | to | 12:00 | 5 | 10:00 | to | 12:00 | 6 | 10:00 | to | 11:00 | 2
|  | Avg | 6 |  |  | Avg | 4 |  |  | Avg | 3 |  |  | Avg | 5 |  |  | Avg | 7 |  |  | Avg | 7
|  | Max. | 10 |  |  | Max. | 8 |  |  | Max. | 5 |  |  | Max. | 12 |  |  | Max. | 12 |  |  | Max. | 12

## 5th Fl. AC reading
Consumption details at IDC 5th floor 1.5 Tr split AC
Sl no | Reading start date | Time | KWH | Reading close date | Time | Kwh | Actual KWH | Mode | (KWH) saving | % of Saving
1 | 24/10/2014 | 11:00 | 1292.4 | 25/10/2014 | 11:00 | 1302.6 | 10.2 | Bypass
2 | 25/10/2014 | 11:00 | 1302.6 | 26/10/2014 | 11:00 | 1310.1 | 7.5 | Saver | 2.7 | 26.4706
3 | 26/10/2014 | 11:00 | 1310.1 | 27/10/2014 | 11:00 | 1321 | 10.9 | Bypass
4 | 27/10/2014 | 11:00 | 1321 | 28/10/2014 | 11:00 | 1329.1 | 8.1 | Saver | 2.8 | 25.6881
5 | 28/10/2014 | 11:00 | 1329.1 | 29/10/2014 | 11:00 | 1340.4 | 11.3 | Bypass
6 | 29/10/2014 | 11:00 | 1340.4 | 30/10/2014 | 11:00AM | 1348.9 | 8.5 | Saver | 2.8 | 24.7788
7 | 30/10/2014 | 11:00 | 1348.9 | 31/10/2014 | 11:00AM | 1359.1 | 10.2 | Bypass
8 | 31/10/2014 | 11:00 | 1359.1 | 2014-01-11 | 11:00AM | 1366.8 | 7.7 | Saver | 2.5 | 24.5098
9 | 2014-01-11 | 11:00 | 1366.8 | 2014-02-11 | 11:00AM | 1377.8 | 11 | Bypass